## Sheet1
MASTER LIGHTING SCHEDULE - V2 -4/18/25
FIXTURE NUMBER MOUNTING TYPE:
CL - CEILING MOUNTED CV - COVE MOUNTED GR - GROUND P - POLE/POST R - RECESSED
S - SUSPENDED/SURFACE T - TRACK UC - UNDER CABINET W - WALL MOUNTED
FIXTURE NUMBER |  |  | DESCRIPTION | MANUFACTURER | VOLTAGE | DIMMING | LUMEN | WATTAGE | COLOR TEMPERATURE | INSTALLATION | REMARKS
TROFFERS | R1 | 2X2 | 2' X 2' LED RECESSED TROFFER FIXTURE WITH EXTRUDED ALUMINUM HOUSING, SOFT DIFFUSED ACRYLIC LENS AND UNIVERSAL 0-10V DIMMABLE DRIVER. | METALUX RLN SERIES MARK ARCHITECTURAL WHISPER SERIES FINELITE HPRA-DCO SERIES GE ASSENT SERIES VISCOR LRTG SERIES | UNIV | 0-10V DIMMABLE DRIVER | 3400 | 34 | 3500 | RECESSED MOUNT IN GRID | FIXTURE TO REPLACE: DAY-BRITE SOFTRACE, LITHONIA 2ALL, PINNACLE AD24, LITHONIA 2RTL, AND LITHONIA 2FSL4
| R2 | 2X4 | 2' X 4' LED RECESSED TROFFER FIXTURE WITH EXTRUDED ALUMINUM HOUSING, SOFT DIFFUSED ACRYLIC LENS AND UNIVERSAL 0-10V DIMMABLE DRIVER. | METALUX RLN SERIES MARK ARCHITECTURAL WHISPER SERIES FINELITE HPRA-DCO SERIES GE ASSENT SERIES VISCOR LRTG SERIES | UNIV | 0-10V DIMMABLE DRIVER | 4800 | 41 | 3500 | RECESSED MOUNT IN GRID
| R3 | 2X4 | 2' X 4' LED RECESSED EDGE LIT FLAT PANEL FIXTURE WITH ALUMINUM HOUSING AND UNIVERSAL 0-10V DIMMABLE DRIVER. | METALUX FP SERIES LITHONIA EPANL SERIES DAY-BRITE FPZ SERIES RAB EZPAN SERIES | UNIV | 0-10V DIMMABLE DRIVER | 4800 | 37 | 3500 | RECESSED MOUNT IN GRID
| R4 | PATIENT BED FIXTURE | 2'X 4' RECESSED MULTI-FUNCTION LED PATIENT ROOM TROFFER WITH SEPARATE CONTROL OF AMBIENT, EXAM AND READING FUNCTIONS, COLD ROLLED STEEL HOUSING, SYMMETRIC DIFFUSED OPAL ACRYLIC CENTER BASKET, 0-10V DIMMABLE DRIVER WITH DIMMING TO 1%. FURNISH WITH LOW VOLTAGE CONTROLLER FOR CONTROL VIA NURSE CALL PILLOW SPEAKER. | FAIL SAFE MPR3 SERIES KENALL MPC SERIES HE WILLIAMS MDB SERIES VISCOR MD3G C84G SERIES | UNIV | 0-10V DIMMABLE DRIVER | 2200 READING 4000 AMBIENT 10300 EXAM | 167 | 3500 | RECESSED MOUNT IN GRID
| R5 | 2X4 SURGICAL | 2' X 4' X 4-3/4" DEEP RECESSED SURGICAL TROFFER WITH COLD ROLLED STEEL PAINTED HOUSING, WET LOCATION LISTED, ASYMMETRIC 0.125 LENS, 0-10V DIMMABLE DRIVER WITH DIMMING TO 1%, 90 CRI AND COMPLIES WITH MILSTD 461 | FAIL SAFE ORL SERIES KENALL M4SEDI24 SERIES NEW STAR SS SERIES CERTOLUX MSUI SERIES | UNIV | 0-10V DIMMABLE DRIVER | 26000 | 184 | 3500 | RECESSED IN DRYWALL
| R6 | SEALED CLEANROOM | 2' X 4' SEALED CLEANROOM TROFFER WITH 20 GAUGE COLD ROLLED STEEL HOUSING, #304 STAINLESS STEEL DOOR AND DIFFUSED ACRYLIC LENS. | FAIL SAFE CLM SERIES KENALL CSERO SERIES NEW STAR SCR SERIES CERTOLUX CRU SERIES | UNIV | 0-10V DIMMABLE DRIVER | 5600 | 50 | 3500 | RECESSED
| R7 | BEHAVIORAL HEALTH TROFFER | 2' X 4' LED RECESSED BEHAVIORAL HEALTH TROFFER WITH HEAVY DUTY 14 GAUGE COLD ROLLED STEEL HOUSING, 0.250" CLEAR POLYCARBONATE LENS AND UNIVERSAL 0-10V DIMMABLE DRIVER. FURNISH WITH TORX HEAD SCREWS. | KENALL MMAC SERIES | UNIV | 0-10V DIMMABLE DRIVER | 9000 | 90 | 4000 | RECESSED
| R8 | 2 X 2 HIGH ABUSE | 2'W X 2'L X 5" D RECESSED HIGH ABUSE TROFFER WITH 16 GAUGE COLD ROLLED STEEL HOUSING, 0.250 CLEAR POLYCARBONATE LENS, UNIVERSAL 0-10V DIMMABLE DRIVER. | FAILSAFE FSR SERIES KENALL HASEDI SERIES NEW STAR 57-R SERIES | UNIV | 0-10V DIMMABLE DRIVER | 6000 | 50 | 3500 | RECESSED MOUNT
DOWNLIGHTS | R9 | 4" ROUND | 4" ROUND RECESSED DOWNLIGHT WITH SEMI-SPECULAR REFLECTOR, MEDIUM DISTRIBUTION, 0-10V DIMMABLE DRIVER. | PORTFOLIO LD4B SERIES GOTHAM EVO SERIES PRESCOLITE LTR SERIES HE WILLIAMS 4DR SERIES LIGHTOLIER P4R SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1500 | 16 | 3500 | RECESSED MOUNT IN GRID
| R10 | 4" ROUND LENSED | 4" ROUND RECESSED DOWNLIGHT WITH DIFFUSED FROSTED ACRYLIC LENS, SEMI-SPECULAR REFLECTOR, MEDIUM DISTRIBUTION, 0-10V DIMMABLE DRIVER WITH DIMMING TO 1%. | PATHWAY 4VL SERIES GOTHAM EVOP SERIES `SPECTRUM GV SERIES PEACHTREE 4BLRD HE WILLIAMS 4DRL SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1500 | 14 | 3500 | RECESSED MOUNT
| R11 | 6" ROUND | 6" ROUND RECESSED DOWNLIGHT WITH SEMI-SPECULAR REFLECTOR, MEDIUM DISTRIBUTION, 0-10V DIMMABLE DRIVER. | PORTFOLIO LD6B GOTHAM EVO SERIES LIGHTOLIER P6R SERIES `HE WILLIAMS 6DR SERIES PRESCOLITE LTR-6RD SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1500 | 15 | 3500 | RECESSED MOUNT
| R12 | 6" ROUND WALL WASH | 6" ROUND RECESSED WALL WASH DOWNLIGHT WITH SEMI-SPECULAR REFLECTOR, 0-10V DIMMABLE DRIVER. | PORTFOLIO LD6B SERIES GOTHAM EVOWW SERIES PRESCOLITE LTR-6RW SERIES `HE WILLIAMS 6DR-WW SERIES LIGHTOLIER P6R-LW SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1500 | 16 | 3500 | RECESSED MOUNT
| R13 | 6" ROUND LENSED | 6" ROUND RECESSED DOWNLIGHT WITH DIFFUSED FROSTED ACRYLIC LENS, SEMI-SPECULAR REFLECTOR, MEDIUM DISTRIBUTION, 0-10V DIMMABLE DRIVER WITH DIMMING TO 1%. | PATHWAY LIGHTING 6VL SERIES GOTHAM EVO6P SERIES SPECTRUM GV SERIES HE WILLIAMS 6DR SERIES PEACHTREE 6BLRD SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1500 | 15 | 3500 | RECESSED MOUNT
| R14 | SHOWER | 6" ROUND LED RECESSED SHOWER DOWNLIGHT WITH BOTTOM NON CONDUCTIVE DIFFUSED LENS AND DEAD FRONT TRIM. | PORTFOLIO LDS6B SERIES KIRLIN LIGHTING MRR SERIES GOTHAM EVOSH SERIES PRESCOLITE LTR-6RDSH SERIES HE WILLIAMS 6DR-S LIGHTOLIER P6R-SL SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1000 | 9 | 3500 | RECESSED MOUNT
| R15 | SHALLOW PLENUM DOWNLIGHT | 6" ROUND SHALLOW PLENUM DOWNLIGHT WITH REMOTE DRIVER, POLYCARBONATE LENS AND WHITE TRIM FINISH. | LITHONIA WF6 SERIES | 120V | 0-10V DIMMABLE DRIVER | 1000 | 13 | 3500 | RECESSED MOUNT
| R16 | 6" MRI | 6" NON FERROUS RECESSED MRI DOWNLIGHT WITH MEDIUM DISTRIBUTION, FURNISH COMPLETE SYSTEM WITH SMART FILTERS AND POWER SUPPLIES | KIRLIN MRR-05420 SERIES KENALL RL591 SERIES | UNIV | 0-10V DIMMABLE DRIVER | 2400 | 35 | 3500 | RECESSED MOUNT IN GRID
| R17 | SURGICAL DOWNLIGHT | 6" ROUND SEALED DOWNLIGHT WITH MEDIUM DISTRIBUTION, ANTIMICROBIAL MATTE WHITE FINISH, BOTTOM ENCLOSED LENS, 0-10V DIMMABLE DRIVER WITH DIMMING TO 1%, RFI GRID AND COMPLIES WITH MILSTD 461 | FAIL SAFE FLD6B SERIES GOTHAM EVOSG SERIES KENALL M4DL6 SERIES NEW STAR DLM SERIES | UNIV | 0-10V DIMMABLE DRIVER | 2000 | 21 | 3500 | RECESSED MOUNT IN GRID
| R18 | DOWNLIGHTS | ADJUSTABLE LED DOWNLIGHTS IN RECESSED STEEL HOUSING, MEDIUM BEAM OPTICS, AND WHITE FINISH | RSA MRZ SERIES LF ILLUMINATION MF300 SERIES WAC MT-4 SERIES NORA NM10 SERIES AMERLUX HORNET SERIES | UNIV | 0-10V DIMMABLE DRIVER |  |  | 3000 | RECESSED
| R19 | 6" ROUND DOWNLIGHT | 6" ROUND DOWNLIGHT WITH 0.187" CLEAR POLYCARBONATE LENS, VANDAL RESISTANT HOUSING, MATTE WHITE FINISH AND UNIVERSAL 0-10V DIMMABLE DRIVER | FAILSAFE FLD6B SERIES | UNIV | 0-10V DIMMABLE DRIVER | 2000 | 21 | 4000 | RECESSED
LINEAR | R20 | 4" RECESSED | 4"W X 48"L X 4-1/2"D LED LINEAR WITH FLUSH SATIN LENS, EXTRUDED ALUMINUM HOUSING, DIRECT DISTRIBUTION AND 0-10V DIMMABLE DRIVER | NEORAY DEFINE 4 SERIES MARK ARCHITECTURAL LIGHTING SLOT 4 SERIES FINELITE HP4 SERIES HE WILLIAMS MX4R SERIES PINNACLE EDGE EV4D SERIES PRUDENTIAL P44 SERIES | UNIV | 0-10V DIMMABLE DRIVER | 3200 | 32 | 3500 | RECESSED MOUNT IN GRID
| R21 | 4" WALL WASH | 4" WIDE RECESSED LED WALL WASH LINEAR FIXTURE WITH ALUMINUM HOUSING | PINNACLE EV3WW SERIES HE WILLIAMS PX WASH SERIES | UNIV | 0-10V DIMMABLE DRIVER | 3200 | 50 | 3500 | RECESSED MOUNT IN GRID
| R22 | 4" WALL WASH PERIMETER | 4" WIDE RECESSED LED WALL WASH PERIMETER MOUNTED FIXTURE WITH EXTRUDED ALUMINUM HOUSING, FROSTED ACRYLIC LENS AND WHITE FINISH. COORDINATE LENGTH WITH ARCHITECTURAL DRAWINGS. | FOCAL POINT FOCUS SERIES MARK LIGHTING SP SERIES LITECONTROL 4L-WS SERIES PAL MLR SERIES HE WILLIAMS PX WASH SERIES | UNIV | 0-10V DIMMABLE DRIVER | 3200 | 50 | 3500 | PERIMETER MOUNT
| R23 | 4" PERIMETER | 4" WIDE RECESSED LED FIXTURE WITH DIRECT DISTRIBUTION, EXTRUDED ALUMINUM HOUSING, FLUSH ACRYLIC LENS AND WHITE FINISH. COORDINATE LENGTH WITH ARCHITECTURAL DRAWINGS. | FOCAL POINT TRACE SERIES AXIS BEAM 4 BBPRLEDPAT SERIES PRUDENTIAL BIONIC PRO SERIES LITECONTROL 4L-WS SERIES HE WILLIAMS PX SLOT SERIES PINNACLE EDGE EVL SERIES | UNIV | 0-10V DIMMABLE DRIVER | 700 LUMEN/FT | 7 WATTS/ FT | 3500 | RECESSED MOUNT IN GRID
| R24 | 3" RECESSED | 3" WIDE X 48" LONG X 4-1/2" DEEP LED LINEAR WITH FLUSH SATIN LENS, EXTRUDED ALUMINUM HOUSING, AND 0-10V DIMMABLE DRIVER | NEORAY DEFINE 3 SERIES AXIS BEAM 3 SERIES LITE CONTROL 3L-RD SERIES FORUM SAR-F SERIES LEDALITE TRUEGROOVE SERIES | UNIV | 0-10V DIMMABLE DRIVER | 800 LUMEN/FT | 28 | 3500 | RECESSED MOUNT IN GRID
| R25 | 6" RECESSED | 6" W X 48"L X 4-3/8"D RECESSED LED LINEAR WITH COLD ROLLED STEEL HOUSING, WHITE FINISH, FLUSH FROSTED LENS, STANDARD DISTRIBUTION AND 0-10V DIMMABLE DRIVER. | FOCAL POINT SEEM 6 SERIES MARK ARCHITECTURAL LIGHT SLOT 6 SERIES FINELITE HP6 SERIES HE WILLIAMS LL6 SERIES PINNACLE EDGE EV6 SERIES | UNIV | 0-10V DIMMABLE DRIVER | 4800 | 40 | 3500 | RECESSED MOUNT IN GRID
| R26 | LINEAR | RECESSED HIGH IMPACT LINEAR WITH WHITE FINISH AND LENS. FURNISH WITH TAMPER RESISTANT SCREWS. | SELUX M125 | UNIV | 0-10V DIMMABLE DRIVER | 730 LUMEN/FT | 8 WATTS/FT | 3500 | RECESSED
| R27 | STEP NIGHT LIGHT | 6" X 9" RECESSED NIGHT LIGHT WITH AMBER LED, 0.125" INNER PRISMATIC LENS. 0.250" CLEAR POLYCARBONATE OUTER LENS, WHITE HOUSING AND TORX HEAD TAMPER PROOF SCREWS. | KENALL RFW SERIES | UNIV | - |  | 2 | 3500 | RECESSED IN WALL
LINEAR | S1 | 4" PENDANT | 4" WIDE LED PENDANT FIXTURE WITH ALUMINUM HOUSING, WHITE FINISH, FLUSH DIFFUSED LENS, DIRECT AND INDIRECT OUTPUT, AND 0-10V DIMMABLE DRIVER. | NEORAY DEFINE SERIES AXIS BEAM 4 SERIES FINELITE HP4 SERIES HE WILLIAMS MX4UD SERIES PINNACLE EDGE EX4DI | UNIV | 0-10V DIMMABLE DRIVER | 800 LUMEN/FT DOWN 800 LUMEN/FT UP | 52 | 3500 | AIR CRAFT CABLE SUSPENDED
| S2 | 4" PENDANT WALL WASH | 4" WIDE LED PENDANT FIXTURE WITH DIRECT AND INDIRECT OUTPUT. | FOCAL POINT SEEM 4 SERIES AXIS BEAM 4 SERIES FINELITE HP4 SERIES PINNACLE EX3BWW SERIES HE WILLIAMS M4D SERIES | UNIV | 0-10V DIMMABLE DRIVER | 24 | 1320 | 3500 | AIR CRAFT CABLE SUSPENDED
| S3 | 2" PENDANT | 2" WIDE PENDANT MOUNTED LED LINEAR WITH ALUMINUM HOUSING, DIRECT AND INDIRECT DISTRIBUTION | LUMENWERX VIA 2 SERIES AXIS BEAM 2 SERIES LITECONTROL 2L-P-ID SERIES HE WILLIAMS MX2UD SERIES PINNACLE EDGE 2 SERIES | UNIV | 0-10V DIMMABLE DRIVER | 600 LUMEN/FT DOWN 400 LUMEN/FT UP | 10 WATTS/FT | 3500 | AIR CRAFT CABLE SUSPENDED
| S4 | 3" PENDANT | 3" WIDE PENDANT MOUNTED LED LINEAR WITH ALUMINUM HOUSING, WHITE FINISH, DIRECT DISTRIBUTION, FLUSH ACRYLIC LENS AND 0-10V DIMMABLE DRIVER. | NEORAY DEFINE 3 SERIES AXIS BEAM 3 SERIES LITECONTROL 3L-P-D SERIES LEDALITE TRUEGROOVE SERIES FORUM SAD33 SERIES | UNIV | 0-10V DIMMABLE DRIVER | 4000 | 42 | 3500 | AIR CRAFT CABLE SUSPENDED
| S5 | UTILITY | 3" WIDE X 48" LONG LED STRIP LIGHT WITH ROUND FROSTED LENS, STEEL HOUSING, CHAIN HANG TO MISS OBSTRUCTIONS. | METALUX SNLED SERIES LITHONIA ZL1N SERIES COLUMBIA CSL SERIES HE WILLIAMS 75 LED SERIES DAY BRITE FSS SERIES | UNIV | - | 4100 | 35 | 3500 | CHAIN HANG
| S6 | 4" CYLINDER | 4" ROUND X 12-1/2" HIGH PENDANT STEM MOUNT CYLINDER WITH ALUMINUM HOUSING AND UNIVERSAL 0-10V DIMMING | SSL SSC4 SERIES METEOR AS4 SERIES ALW CORE 300 SERIES HE WILLIAMS 4CR SERIES VANTAGE 412 FCRU SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1600 | 50 | 3500 | PENDANT
| S7 | 8" CYLINDER | 8" ROUND X 14" DEEP AIR CRAFT CABLE SUSPENDED LED CYLINDER WITH ALUMINUM HOUSING, WHITE FINISH, MEDIUM DISTRIBUTION, SEMI-SPECULAR REFLECTOR AND 0-10V UNIVERSAL DIMMABLE DRIVER | SSL SSC8 SERIES GOTHAM EVO CYL SERIES PRESCOLITE LCC8LED SERIES HE WILLIAMS 8CR SERIES VANTAGE 8140BLED SERIES | UNIV | 0-10V DIMMABLE DRIVER | 2000 | 32 | 3500 | AIR CRAFT CABLE SUSPENDED
| S8 | DIRECT/ INDIRECT PENDANT | 8-1/4"W X 96"L X 1-3/4"D PENDANT FIXTURE WITH CENTER DIFFUSED LENS, DIRECT AND INDIRECT DISTRIBUTION, COLD ROLLED STEEL HOUSING, WHITE FINISH AND AIR CRAFT CABLE SUSPENSION KIT | LITHONIA GRAD LINEAR CORELITE JAYLUM J2 SERIES LITECONTROL SAE104 SERIES HE WILLIAMS SD15 SERIES PINNACLE LINERO SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1300 LUMEN / FT | 40 | 3500 | AIR CRAFT CABLE SUSPENDED
| S9 | PENDANT RING | 54" ROUND LED PENDANT RING WITH ALUMINUM HOUSING, INDIRECT OPTICS, MATTE WHITE FINISH, 0-10V DIMMABLE DRIVER AND AIR CRAFT CABLE SUSPENSION KIT. | EUREKA CYCLE 4800 SERIES ALW MR3 SERIES WESTPORT JANUS-R SERIES SOLERA CIRC II SERIES TMS ORBITA I SERIES | 277V | 0-10V DIMMABLE DRIVER | 2900 | 48 | 3500 | AIR CRAFT CABLE SUSPENDED | DRIVER TO BE LOCATED IN ACCESSIBLE LOCATION. COORDINATE LOCATION WITH OWNER PRIOR TO INSTALLATION.
` | S10 |  | 4' ROUND LED PENDANT RING FIXTURE WITH DIRECT DISTRIBUTION, DIFFUSED POLYCARBONATE LENS, WHITE FINISH, CENTER CANOPY SUSPENDED, AND 0-10V DIMMABLE DRIVER. COORDINATE SUSPENSION HEIGHT WITH ARCHITECT. | OCL SOLO SERIES ALW MOONRING LP1 SERIES DELRAY UNO SERIES WESTPORT ECLIPSE SERIES AXOLIGHT ULIGHT SERIES | UNIV | 0-10V DIMMABLE DRIVER | 2300 | 58 | 3500 | AIR CRAFT CABLE SUSPENDED | DRIVER TO BE LOCATED IN ACCESSIBLE LOCATION. COORDINATE LOCATION WITH OWNER PRIOR TO INSTALLATION.
| S11 |  | 24" ROUND X 3"H AIRCRAFT CABLE SUSPENDED CIRCULAR RING | CORONET LS CURVE SERIES BARBICAN MODULAR CIRCLE SERIES | 277V | 0-10V DIMMABLE DRIVER |  |  | 3500 | AIR CRAFT CABLE SUSPENDED | DRIVER TO BE LOCATED IN ACCESSIBLE LOCATION. COORDINATE LOCATION WITH OWNER PRIOR TO INSTALLATION.
| S12 |  | 36" CUSTOM 3 TIER DONUT RING. AIRCRAFT CABLE SUSPENDED. COORDINATE EXACT MOUNTING AND FINISH WITH ARCHITECT. | BARBICAN MODULAR CIRCLE SERIES LIGHTING ELEMENTS ANDROMEDA SERIES | 277V | 0-10V DIMMABLE DRIVER |  | 40 WATT PER FIXTURE | 3500 | AIR CRAFT CABLE SUSPENDED | DRIVER TO BE LOCATED IN ACCESSIBLE LOCATION. COORDINATE LOCATION WITH OWNER PRIOR TO INSTALLATION.
| S13 | PENDANT | 5" ROUND X 8" H DECORATIVE LED PENDANT WOOD FINISH AND OPAL GLASS LENS, SUSPENDED CORD MOUNT. | MATER TERHO SERIES | 120V | - |  | 9 |  | CORD MOUNTED
| S14 | PENDANT | LED DROP SHAPE PENDANT WITH WOOD FINISH, CORD MOUNT SUSPENDED, COORDINATE HEIGHT WITH ARCHITECT. | MATER LIUKU BASE | 120V | - |  | 9 |  | CORD MOUNTED
| S15 | TRACK LIGHT | 5-1/2" X 3-3/4" SUSPENDED TRACK LIGHT WITH ALUMINUM HOUSING, WHITE FINISH AND ACRYLIC LENS | CONTECH CTL18H SERIES SPECTRUM LIGHTING TWH4FX SERIES NORA NTE-8803 SERIES LIGHTOLIER LWW SERIES | 120 | 0-10V DIMMABLE DRIVER | 2200 | 20 | 3500 | MOUNT ON SUSPENDED TRACK
| S16 | VANDAL RESISTANT | 8-1/4"W x 54"L X 4"D LED VANDAL RESISTANT FIXTURE WITH FROSTED POLYCARBONATE LENS AND INTERNAL CLEAR LENS, WIDE DISTRIBUTION, WET LOCATION LISTING AND 0-10V DIMMABLE DRIVER. PENDANT MOUNT TO MISS OBSTRUCTIONS. | METALUX 4VT2 SERIES LITHONIA VAP SERIES COLUMBIA LXEM SERIES HE WILLIAMS 96 SERIES DAY-BRITE DW SERIES | UNIV | 0-10V DIMMABLE DRIVER | 4000 | 33 | 3500 | PENDANT
| S17 | HIGH BAY | 1' X 4' LED PENDANT MOUNTED HIGH BAY FIXTURE WITH 20 GAUGE STEEL HOUSING. FURNISH WITH SWIVEL STEM KIT AND BRACKETS FOR PENDANT MOUNTING | METALUX 4ILED SERIES LITHONIA MSL SERIES COLUMBIA RLB SERIES GE ABC1 SERIES VISCOR LHBD SERIES | UNIV | 0-10V DIMMABLE DRIVER | 10000 | 86 | 3500 | STEM PENDANT MOUNT
| S18 | HIGH BAY | LED HIGH BAY WITH STEEL HOUSING, ACRYLIC LENS, SUITABLE FOR TEMPERATURES OF -40F TO 131F. PENDANT MOUNT | METALUX VHB SERIES LITHONIA IBG SERIES COLUMBIA PEL SERIES LSI AHB SERIES DAY BRITE HBY SERIES | UNIV | 0-10V DIMMABLE DRIVER | 24000 | 144 | 3500 | PENDANT
| S19 | HIGH BAY | 16" ROUND X 16"D HIGH BAY FIXTURE WITH ALUMINUM HOUSING, DAMP LOCATION LISTED, FROSTED ACRYLIC REFLECTOR, FLAT PRISMATIC LENS, AND 0-10V DIMMABLE DRIVER. FURNISH WITH SWIVEL STEM KIT. | LITHONIA JCBL SERIES DAY-BRITE RBX SERIES COLUMBIA UTB2 SERIES | UNIV | 0-10V DIMMABLE DRIVER | 12000 | 90 | 3500 | STEM PENDANT
| S20 | PARKING LOT | 18-1/2" ROUND X 5" DEEP SURFACE MOUNTED PARKING LOT FIXTURE WITH ALUMINUM HOUSING, FLAT DIFFUSED POLYCARBONATE LENS , WIDE DISTRIBUTION, IP66 RATED, AND WHITE FINISH. SURFACE MOUNT TO JUNCTION BOX. | MCGRAW-EDISON TT TOPTIER SERIES GARDCO SVPG SERIES | UNIV | - | 4500 | 34 | 4000 | SURFACE MOUNT
| S21 | CANOPY LINEAR | 2-1/2"W X 48"L X 2-1/2"D EXTERIOR LED WALL GRAZIER WITH EXTRUDED ALUMINUM HOUSING, CLEAR UV POLYCARBONATE LENS, 10 X 60 DEGREE BEAM ANGLE. POSITION FIXTURE TO WASH CANOPY GLASS. | PHILIPS COLOR KINETICS EW GRAZE QLX | UNIV | - | 916 | 20 | 4000 | SURFACE MOUNT
| S22 | GLOBE | 5" ROUND X 10-5/8" DEEP EXTERIOR LED VAPOR TIGHT GLOBE WITH SEAL AND GASKETED CAST ALUMINUM HOUSING, FROSTED GLASS LENS AND GREY FINISH | LITHONIA OLVTWM SERIES TRACELITE TLED804 SERIES COLUMBIA VWGL-2 SERIES CANLET LEDVP SERIES FME JJ-1 SERIES | UNIV | - | 600 | 15 | 4000 | SURFACE MOUNT
| S23 | PENDANT | 10.23" EIKON BASIC PENDANT | SND1358297 | UNIV |  | Bulb Not Included | 10 | 120V | Pendant
| S24 | PENDANT | CLEAR COIL M1-3 - STYLE M2 - 9" DIA x 13" 2.5LBS - Color White | ENGINEER TO CHOOSE LUMENS AND WATTAGE VERIFY WITH NCH PM | UNIV
| W1 | EXIT LIGHT | WALL MOUNTED LED EXIT LIGHT WITH BRUSHED ALUMINUM FINISH AND WHITE HOUSING, AC ONLY AND RED LETTERING. ARROWS AND FACES SHALL BE AS INDICATED ON DRAWINGS. | LITHONIA LE SERIES | UNIV | - | - | 4 | - | WALL MOUNT
| W2 | STRIP LIGHT | 3" WIDE X 48" LONG LED STRIP LIGHT WITH ROUND FROSTED LENS, STEEL HOUSING, CHAIN HANG TO MISS OBSTRUCTIONS. | METALUX SNLED SERIES LITHONIA ZL1N SERIES COLUMBIA CSL SERIES HE WILLIAMS 75 LED SERIES DAY BRITE FSS SERIES | UNIV | - | 4100 | 35 | 3500 | WALL MOUNT ABOVE DOOR
| W3 | STRIP LIGHT | 3" WIDE X 48" LONG SURFACE MOUNTED FIXTURE WITH INTEGRATED OCCUPANCY SENSOR, FULLY FROSTED LENS | METALUX SWLED SERIES LITHONIA WL4 SERIES COLUMBIA ESL SERIES DAY-BRITE FSW SERIES | UNIV | 0-10V DIMMABLE DRIVER | 3000 | 29 | 3500 | WALL MOUNT
| W4 | EGRESS | EMERGENCY EGRESS LIGHT WITH THERMOPLASTIC HOUSING, TWO HEADS, POLYCARBONATE LENS AND SEALED MAINTENANCE FREE NICKEL CADMIUM BATTERY. | SURELITE APEL SERIES LITHONIA ELM2 SERIES DUAL LITE LZ SERIES EXITRONIX QMR SERIES EMERGI-LITE EL-2RHL SERIES | UNIV | - | - | 3 | - | WALL MOUNT
| W5 | EGRESS | EMERGENCY EGRESS LIGHT WITH STEEL HOUSING, TWO LED HEADS, POLYCARBONATE LENS, MAINTENANCE FREE NICKEL CADMIUM BATTERY AND SELF DIAGNOSTICS OPTION. | SURE-LITES NCB SERIES LITHONIA ELT SERIES EXITRONIX RS SERIES | UNIV | - | - | 3 | - | WALL MOUNT
| W6 | 4" CYLINDER | 4" ROUND X 12-1/2" HIGH WALL MOUNTED CYLINDER WITH ALUMINUM HOUSING, WHITE FINISH AND UNIVERSAL 0-10V DIMMING | SSL SSC4 SERIES ALW CORE 300 SERIES HE WILLIAMS 4CRDI SERIES VANTAGE 412BLED SERIES | UNIV | 0-10V DIMMABLE DRIVER | 1300 | 12 | 3500 | WALL MOUNT
| W7 | 8" CYLINDER | 8" ROUND X 14" DEEP AIR CRAFT CABLE SUSPENDED LED CYLINDER WITH ALUMINUM HOUSING, WHITE FINISH, MEDIUM DISTRIBUTION, SEMI-SPECULAR REFLECTOR AND 0-10V UNIVERSAL DIMMABLE DRIVER | SSL SSC8 SERIES GOTHAM EVO CYL SERIES PRESCOLITE LCC8LED SERIES HE WILLIAMS 8CR SERIES VANTAGE 8140BLED SERIES | UNIV | 0-10V DIMMABLE DRIVER | 2000 | 32 | 3500 | AIR CRAFT CABLE SUSPENDED
| W8 | SCONCE | WALL MOUNTED LED DECORATIVE SCONCE, WITH 2" CYLINDER WHITE GLASS DIFFUSER WITH SATIN CHROME FINISH. MOUNT ABOVE MIRROR. | BROWNLEE 1476 SERIES EUREKA 3165 SERIES EVERGREEN CYL-DBL SERIES | 277V | - |  | 8 | 3500 | WALL MOUNTED
| W9 | SCONCE | 12" SQUARE X 4" DEEP WALL MOUNTED LED DECORATIVE SCONCE WITH IMAGE PANEL. FURNISH WITH 0-10V DIMMABLE DRIVER. DECORATIVE PANEL TO BE SELECTED BY ARCHITECT | SOLERA TIC-TAC-TOE-MOD SERIES MANNING LIGHTING PLATEAU SERIES EVERGREEN RND SERIES | 277V | 0-10V DIMMABLE DRIVER | 995 | 16 | 3500 | WALL MOUNTED
| W10 | SEALED AND GASKETED | 7"W X 48"L X 4-1/8"D ENCLOSED AND GASKETED VAPOR TIGHT LED FIXTURE WITH FROSTED IMPACT RESISTANT LENS | METALUX VT2 SERIES LITHONIA FEM SERIES COLUMBIA LIGHTING LXEW SERIES HE WILLIAMS 96 SERIES VISCOR LSVB SERIES | UNIV | - | 4000 | 38 | 3500 | WALL MOUNT
| W11 | WRAP AROUND | 4" W X 48"L X 3"D VANDAL RESISTANT LED WRAP AROUND WITH OPAL POLYCARBONATE LENS, MATTE WHITE FINISH AND EMERGENCY BATTERY PACK. | FAILSAFE HVSL4 SERIES KENALL MLRS8 SERIES NEW STAR VIC SERIES | UNIV | - | 9000 | 90 | 3500 | WALL MOUNT
| W12 | EGRESS | 4' ARCHITECTURAL LED EGRESS LIGHT WITH EXTRUDED ALUMINUM HOUSING, DIFFUSED POLYCARBONATE LENS, SILVER FINISH. WALL MOUNT ABOVE DOOR. | SPITZER DFLV SERIES ACUITY AEL SERIES NEW STAR GATEWAY SERIES EVERGREEN GL SERIES | UNIV | - | 3800 | 35 | 4000 | WALL MOUNT ABOVE DOOR
| W13 | BUILDING MOUNT | 8-1/2"H X 17"W X 10"D TRAPEZOID EXTERIOR WALL MOUNTED LED SCONCE WITH COLD WEATHER RATED BATTERY BACK-UP. WALL MOUNT ABOVE DOOR. | LITHONIA WST LED SERIES MCGRAW EDISON IST SERIES GEOPAK 2 SERIES LSI GST SERIES GARDCO 101 SERIES | UNIV | - | 3500 | 25 | 4000 | WALL MOUNTED
| W14 |  | 15-3/4" X 8" X 8" EXTERIOR WALL MOUNTED FIXTURE WITH ALUMINUM HOUSING, DARK BRONZE FINISH, | INVUE ENC SERIES | UNIV | - | 2300 | 26 | 4000 | WALL MOUNTED
| W15 |  | 16-3/8"W X 7-1/8"H X 9"D WALL MOUNTED LED WITH DIE-CAST ALUMINUM HOUSING, ACRYLIC LENS, FORWARD THROW OPTICS | MCGRAW EDISON IMPACT SERIES LITHONIA CSXW SERIES LSI XWM SERIES STONCO LPW32 SERIES | UNV | - | 8000 | 69 | 4000 | WALL MOUNTED | CONTROL BY BAS SYSTEM
| W16 |  | OUTDOOR VAPORTIGHT LED FIXTURE | HUBBELL VWGL SERIES SIGNIFY VWXL SERIES SOLAS RAY UQVL SERIES LITHONIA OLVT SERIES | UNV | - | 757 | 11 | 4000 | WALL MOUNTED
EXIT LIGHTS | CL1 | EXIT LIGHT | CEILING MOUNTED LED EXIT LIGHT WITH BRUSHED ALUMINUM FINISH AND WHITE HOUSING, AC ONLY AND RED LETTERING. ARROWS AND FACES SHALL BE AS INDICATED ON DRAWINGS. | LITHONIA LE SERIES | UNIV | - | - | 4 | - | CEILING MOUNT
| CL2 | BEHAVIORAL HEALTH EXIT LIGHT | CEILING MOUNTED VANDAL RESISTANT LED EXIT SIGN WITH WHITE PAINTED STEEL HOUSING, RED LETTERS AND TAMPER RESISTANT TORX HEAD SCREWS. ARROWS AND FACES SHALL BE AS INDICATED ON DRAWINGS | KENALL MMEX SERIES | UNIV | - | - | 3 | - | CEILING MOUNT
| CL3 | BEHAVIORAL HEALTH EXIT LIGHT | EXTREME VANDAL RESISTANT COLD WEATHER RATED LED EXIT LIGHT WITH NEMA 4X HOUSING, CLEAR UV POLYCARBONATE COVER, SINGLE FACE, WHITE FINISH AND TAMPER RESISTANT T20 TORX HEAD SCREWS. | LITHONIA LV SERIES EXITRONIX NAV SERIES SURELITES UX SERIES DUAL-LITE SEWL SERIES | UNIV | - | - | 4 | - | CEILING MOUNT
| CL4 | SURFACE MOUNTED | 12" ROUND SURFACE MOUNTED EDGE LIT DOWNLIGHT WITH TAMPERPROOF HOUSING, POLYCARBONATE DIFFUSER, WHITE FINISH, 0-10V DIMMABLE DRIVER. FURNISH WITH TILT DRIVER SYSTEM. | LAUREN ILLUMINATION LCLCV | 277/24 | 0-10V DIMMABLE DRIVER | 1320 | 12 |  | SURFACE MOUNTED
| CV1 | COVE | LED COVE LIGHT WITH ADJUSTABLE BASE, CLEAR POLYCARBONATE LENS AND UNIVERSAL DIMMABLE DRIVER. COORDINATE LENGTH WITH ARCHITECTURAL DRAWINGS. | TRAXON COVE AC HO SERIES TROV SLIM L30 SERIES ELIPTIPAR 314 SERIES COLORKINETICS EW COVE QLX SERIES SSL ECOVELINE SL SERIES GE LLW SERIES | 277V | - | 400 LUMEN/ FT | 5 WATT/ FT | 3500 | MOUNT IN ARCHITECTURAL COVE
| CV2 | COVE | 4" WIDE X 2-1/4" DEEP LED COVE LIGHT WITH EXTRUDED ALUMINUM HOUSING, ADJUSTABLE BASE AND UNIVERSAL 0-10V DIMMABLE DRIVER. COORDINATE LENGTH WITH ARCHITECTURAL DRAWINGS. | FOCAL POINT COVERT SERIES ELIPTIPAR S315 SERIES FORUM OCM SERIES PINNACLE COVE SERIES | UNIV | 0-10V DIMMABLE DRIVER | 500 LUMEN/ FT | 5 WATT/FT | 3500 | MOUNT IN ARCHITECTURAL COVE
| T1 | TRACK LIGHT | 12' TRACK SYSTEM WITH 2-1/2" ROUND X 4"D CYLINDER VERTICAL LED TRACK HEADS WITH ALUMINUM HOUSING, ADJUSTABLE AIMING AND WHITE FINISH | JUNO T381L SERIES WAC LIGHTING 1014 SERIES LIGHTOLIER LLAV SERIES LUMENPULSE LATSS SERIES PURE EDGE CLASSIC VERTICAL SERIES LITON APOLLO SERIES TIMES SQUARE CCR SERIES | 120V | - | 1142 PER FIXTURE | 11 PER FIXTURE | 3500 | TRACK MOUNTED
| P1 | POLE MOUNT | 25" ROUND ARM MOUNTED POLE FIXTURE WITH SPUN ALUMINUM HOUSING, DIE CAST ALUMINUM LENS FRAME, LED OPTICS, POLYCARBONATE LENS, 700mA DRIVER CURRENT, TYPE 1 DISTRIBUTION AND WHITE FINISH | KIM CCS25A SERIES | 277V |  | 19000 | 228 | 4000 | 25' ROUND ALUMINUM POLE
| P2 | POLE MOUNT | 17" ROUND ARM MOUNTED POLE FIXTURE WITH SPUN ALUMINUM HOUSING, DIE CAST ALUMINUM LENS FRAME, LED OPTICS, POLYCARBONATE LENS, 3500mA DRIVER CURRENT, TYPE 1 DISTRIBUTION AND WHITE FINISH | KIM CCS17 SERIES | 277V |  |  |  | 4000 | POLE MOUNT
| P3 | POLE MOUNT | POLE TOP LED FIXTURE WITH TYPE 5 DISTRIBUTION, FLAT SOFT LIGHT DIFFUSED ACRYLIC LENS, MDL018 DRIVER, 12L LED AND WHITE FINISH | STERNBERG LIGHTING SOLANA SL660 | UNIV |  |  |  | 4000 | 14' ROUND ALUMINUM POLE
| GR1 | FLOOD LIGHT | EXTERIOR LED FLOOR MOUNTED FLOOD LIGHT WITH ALUMINUM HOUSING, DARK BRONZE FINISH AND 5X4 OPTICS | LITHONIA OLB SERIES HADCO BL9 SERIES WAC 5012 SERIES VISTA PRO 3107 SERIES LIGMAN UZA-50001 SERIES | UNIV | - | 600 | 11 | 4000 | GROUND MOUNTED
| GR2 | IN GROUND LINEAR | 2" W X 5-1/2" LONG LED LINEAR EXTERIOR IN GROUND WALL GRAZER WITH EXTRUDED ALUMINUM HOUSING, GREY FINISH, IP67 RATED. | IGUZZINI LINEALUCE MINI SERIES PIL STRIP SQUARE INGROUND 550 SERIES LUMENPULSE LOI SERIES GVA STR9 IG SERIES COLOR KINETICS GRAZE SERIES | UNIV | - | 360 LUMEN /FT | 3.5 WATT/ FT | 4000 | IN GROUND
| UC1 | UNDER CABINET | 48" LED UNDER CABINET LIGHT WITH SMOOTH ACRYLIC LENS AND MATTE WHITE FINISH | FAILSAFE UCL SERIES AIREY-THOMPSON 13HC SERIES KENALL AUCLED SERIES HE WILLIAMS 1SF SERIES DAY-BRITE LINCS SERIES | UNIV | 0-10V DIMMABLE DRIVER | 2000 | 20 | 3500 | MOUNT TO UNDERSIDE OF CABINET
FIXTURE NOTES:
1. | FIXTURES INDICATED ARE BASIS OF DESIGN FOR EACH TYPE. VARIATIONS IN DIMENSIONS, COLOR TEMPERATURE, LUMEN OUTPUT, MOUNTING, ACCESSORIES, ETC. ARE PROJECT DEPENDANT AND SHALL BE COORDINATED WITH THE HOSPITAL.
2. | VARIATIONS IN FIXTURE TYPE SHALL BE ADDED TO THE PROJECT SCHEDULE SEQUENTUALLY BY LETTER, I.E. R1A, R1B, ETC.
3. | MINIMUM COLOR RENDERING INDEX (CRI) SHALL BE 80.
4. | INTERIOR LIGHTING SHALL BE CONTROLLED BY LOCAL LOW VOLTAGE CONTROL SYSTEM. WIRELESS, CLOUD BASED OR SYSTEMS THAT REQUIRE NETWORK ACCESS ARE NOT ACCEPTABLE.
| A. | LOW VOLTAGE CONTROLS SHALL CONSIST OF WALL MOUNTED SWITCHES AND SLIDE DIMMERS, WALL AND CEILING MOUNTED OCCUPANCY SENSORS, POWER PACKS.
| B. | OCCUPANCY SENSORS SHALL BE DUAL TECHNOLOGY
| C. | CEILING MOUNTED OCCUPANCY SENSORS SHALL HAVE AUXILIARY RELAY
| D. | ACUITY NLIGHT SERIES (WIRED) SHALL BE THE BASIS OF DESIGN. OTHER ACCEPTABLE MANUFACTURERS ARE: WATTSTOPPER DLM SERIES, HUBBELL NX SERIES OR COOPER GREENGATE SERIES.
5. | EXTERIOR LIGHTNG SHALL BE CONTROLLED BY LOCAL LIGHTING CONTACTOR WITH HAND-OFF-AUTO CONTROLS. AUTOMATIC CONTROL SHALL BE THROUGH THE CAMPUS BAS SYSTEM VIA A CENTRALLY LOCATED PHOTO-ELECTRIC SENSOR. LOCAL (HAND) CONTROL SHALL BE AHEAD OF AND OVERRIDE AUTOMATIC CONTROLS.